Date
SECTION 40 95 23

Project Number
PROCESS MONITORING SYSTEM EXPANSION MODULES

Project Name
Page 1

PART 1 GENERAL

1.1 DESCRIPTION
A. Section Includes

1. Expansion modules for process monitoring systems installed in water resource recovery facilities. 
B. Scope

1. Furnish, install, configure, and place into satisfactory operation process monitoring system expansion modules as shown on the Drawings and specified herein.

2. The Drawings and Specifications illustrate and specify functional and general construction requirements of expansion modules and associated networks but do not necessarily show or specify all components, wiring, piping, and accessories required to make a completely integrated system.  Provide all components, piping, wiring, accessories, and labor required for a complete and integrated process monitoring and control system.

C. Coordination:  Coordinate with other suppliers for installation of all items specified herein and required to ensure the complete and proper interfacing of all process monitoring and control network components and systems.
1.2 SYSTEM DESCRIPTION

A. Design Requirements

1. Design process monitoring system expansion modules for continuous operation outdoors.

2. Design process monitoring system expansion modules to stack-mount directly to process monitoring system expansion modules specified in this section and terminal/controllers and process monitoring system expansion modules specified in Section 40 94 13 Process Monitoring System Universal Controllers.

3. Process monitoring system expansion modules shall be designed to be part of a network that has the following capabilities and features:
a. Enhanced protection from overvoltage due to lightning and power supply fluctuations according to EN 61326 when installed using manufacturer’s recommended components per manufacturer’s instructions. 
b. Powered from a centralized power supply.
c. Modular:  Process monitoring system expansion modules shall have full functionality from any location in the network.  
d. Line, tree, star, and multiple star topology.
e. 24VDC loop powered communication.

B. Performance Requirements
1. Operating range

a. Temperature:  -4°F to 131°F (-20°C to 55°C)
b. Relative humidity:  less than or equal to 90% (yearly average)

c. Altitude:  less than or equal to 6,562 ft. (2,000 m) above mean sea level
1.3 QUALITY ASSURANCE
A. Acceptable Manufacturers: 

1. Furnish process monitoring system expansion modules by the named manufacturers. 

2. The named manufacturers have been specified to establish the standard of quality and performance of the equipment to be supplied. 
3. Manufacturer shall be ISO 9001 certified.
1.4 PRODUCT DELIVERY, STORAGE, AND HANDLING

A. Process monitoring system expansion modules shall not be delivered to the site until all product information and system shop drawings have been approved.
B. Delivery and Acceptance Requirements:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer. 

C. Storage and Handling Requirements: 
1. Store and handle materials in accordance with manufacturer’s instructions.
2. Keep materials in manufacturer’s original, unopened containers and packaging until installation.
3. Store materials in clean, dry area indoors.
4. Protect materials during storage, handling, and installation to prevent damage.

5. Temperature range for storage:  -13°F to 149°F (-25°C to 65°C)
1.5 SUBMITTALS

A. Product data

1. Operating manual for process monitoring system expansion module and associated modules.

2. Mounting bracket installation instructions.

B. Manufacturer’s Certifications:  Submit manufacturer’s certification that materials comply with specified requirements and are suitable for intended application.
C. Warranty documentation:  Submit manufacturer’s standard warranties.
PART 2 PRODUCTS

2.1 MANUFACTURER

A. Provide products from the following manufacturer:

1. YSI Incorporated, 1700/1725 Brannum Lane, Yellow Springs, OH  45387.  1-800-765-4974.

2.2 MANUFACTURED UNIT  

A. Process monitoring system expansion modules consist of the following:

1. Expansion modules
a. SensorNet connections
1) Model MIQ/JB, Model MIQ/JBR:  4 SensorNet connections.
2) Model MIQ/PS, Model MIQ/24V, Model MIQ/IF232, Model MIQ/WL PS Set:  3 SensorNet connections.

3) All other models MIQ:  2 SensorNet connections.
b. Power Supply
1) Model MIQ/PS, MIQ/WL PS Set:  100..240VAC.
2) Model MIQ/24V:  24V AC/DC.
c. Current inputs

1) Model MIQ/IC2:  2 current inputs
2. Output modules

a. Relay outputs

1) Model MIQ/CR3:  3 relay outputs

2) Model MIQ/R6:  6 relay outputs

b. Current outputs

1) Model MIQ/CR3:  3 current outputs

2) Model MIQ/C6:  6 current outputs

c. Transmitter Power
1) Model MIQ/IC2:  1 24V power supply output.
d. Digital communications

1) Model MIQ/2-MOD:  RS485 interface for Modbus RTU. 

2) Model MIQ/2-PR:  RS485 interface for Profibus DP(V0) or Profibus DPV1. 

3) Model MIQ/MC2:  Ethernet RJ45 interface for Modbus TCP or Ethernet/IP.
3. S/N terminator switch.

4. Status lights:  yellow LED, red LED.

5. Cable glands:  M 16 x 1.5, 4 total, with screw plug.
2.3 MATERIALS
A. Housing material:  polycarbonate, 20% glass filled
B. EMI/RFI conformance

1. EN 61326 Class B.
2. FCC Class A.
C. Safety

1. Certification: CE, cETLus

D. Protection rating
1. Modules:  IP66.
2. USB, Ethernet interfaces:  IP67

E. 3-year warranty
2.4 ACCESSORIES
A. Rail mounting kit

1. YSI Model 109 286Y.

B. Sun shield 
1. YSI Model 109 295Y sun shield.

2. YSI Model 109 284Y sun shield for junction boxes.

[image: image1]
C. YSI Model 109 284Y sun shield for modules. D-SUB connector [MIQ/2-MOD, MIQ/2-PR]

1. Phoenix Contact VS-09-PROFB (YSI model 902 888Y)
PART 3 EXECUTION

3.1 INSTALLATION

A. Install process monitoring system expansion modules in strict accordance with the manufacturer’s instructions and recommendations.
3.2 DEMONSTRATION AND TRAINING
A. Manufacturer’s representative will include a half-day of training, if requested, for the process monitoring system inclusive of the equipment supplied in this section and Section 40 94 13 Digital Process monitoring system Computers and sections specifying primary process measurement devices.

1. Contractor will schedule a date and time for start-up.

2. Contractor will require representatives of the following be present during the start-up:

a. General contractor

b. Electrical contractor

c. YSI factory-trained representative

d. Owner’s personnel

e. Engineer

END OF SECTION

Note to specifier:  Item 295Y is required for mounting MIQ/WL Set (wireless) modules.









